## errors
Error Code	Error Index	Subsystem Index	Subsystem	Error Message	Code
0101	1	1	Reservoir	VL53L0X No Connect!	#define RESERVOIR_VL53L0X_NO_CONNECT 0x0101 //VL53L0X No Connect!
0102	2	1	Reservoir	No Reservoir DS18B20 Address!	#define RESERVOIR_NO_DS18B20_ADDRESS 0x0102 //No Reservoir DS18B20 Address!
0103	3	1	Reservoir	No Reservoir DS18B20 Read!	#define RESERVOIR_NO_DS18B20_READ 0x0103 //No Reservoir DS18B20 Read!
0104	4	1	Reservoir	Reservoir Open Loop!	#define RESERVOIR_OPEN_LOOP 0x0104 //Reservoir Open Loop!
0105	5	1	Reservoir	Reservoir Level Low!	#define RESERVOIR_LEVEL_LOW 0x0105 //Reservoir Level Low!
0106	6	1	Reservoir	Pump On With No Flow!	#define RESERVOIR_PUMP_ON_WITH_NO_FLOW 0x0106 //Pump On With No Flow!
0107	7	1	Reservoir	Reservoir Temp Too High!	#define RESERVOIR_TEMP_TOO_HIGH 0x0107 //Reservoir Temp Too High!
0107	8	1	Reservoir	Reservoir Temp Too Low!	#define RESERVOIR_TEMP_TOO_LOW 0x0107 //Reservoir Temp Too Low!
0201	1	2	Case	BME280 No Connect!	#define CASE_BME280_NO_CONNECT 0x0201 //BME280 No Connect!
0202	2	2	Case	No Outside DS18B20 Address!	#define CASE_NO_OUTSIDE_DS18B20_ADDRESS 0x0202 //No Outside DS18B20 Address!
0203	3	2	Case	No Outside DS18B20 Read!	#define CASE_NO_OUTSIDE_DS18B20_READ 0x0203 //No Outside DS18B20 Read!
0204	4	2	Case	Display No Connect!	#define CASE_DISPLAY_NO_CONNECT 0x0204 //Display No Connect!
0205	5	2	Case	Outside Temp Too High!	#define CASE_OUTSIDE_TEMP_TOO_HIGH 0x0205 //Outside Temp Too High!
0206	6	2	Case	Outside Temp Too Low!	#define CASE_OUTSIDE_TEMP_TOO_LOW 0x0206 //Outside Temp Too Low!
0207	7	2	Case	Case Temp Too High!	#define CASE_TEMP_TOO_HIGH 0x0207 //Case Temp Too High!
0208	8	2	Case	Case Temp Too Low!	#define CASE_TEMP_TOO_LOW 0x0208 //Case Temp Too Low!
0209	9	2	Case	Case Humidity Too High!	#define CASE_HUMIDITY_TOO_HIGH 0x0209 //Case Humidity Too High!
020A	10	2	Case	Top Fan Low RPM!	#define CASE_TOP_FAN_LOW_RPM 0x020A //Top Fan Low RPM!
020B	11	2	Case	Bottom Fan Low RPM!	#define CASE_BOTTOM_FAN_LOW_RPM 0x020B //Bottom Fan Low RPM!
020C	12	2	Case	Filters Clogged!	#define CASE_FILTERS_CLOGGED 0x020C //Filters Clogged!

## PIDs
PID	Access	DataType	Variable	Units	Alarm Low	Alarm High	Low	High	Description
0	R	bool	digitalRead(ALARMS_RLY)				0	1	Alarm State
1	R	uint16_t	error_code				0	65535	Error Code
2	R	uint16_t	top_fan_reading	RPM			0	6000	Top Fan Tachometer
3	R	uint16_t	bottom_fan_reading	RPM			0	6000	Bottom Fan Tachometer
4	R	uint8_t	fan_pwm_level	%			0	100	Fan PWM
5	R	uint8_t	reservoir_temp_reading	°C	5	30	0	100	Reservoir Temperature
6	R	uint8_t	outside_temp_reading	°C	0	100	0	100	Outside Temperature
7	R	uint8_t	case_temperature_reading	°C	0	100	0	100	Case Temperature
8	R	uint8_t	case_humidity_reading	%RH		80	0	100	Case Humidity
9	R	uint16_t	filterRA.getAverage()	ADC		500	0	1023	Filter Delta P
10	R	uint16_t	reservoir_volume	mL	5800		0	6000	Reservoir Level
11	R	bool	digitalRead(FLOW_SW)				0	1	Flow NOT Detected
12	R	bool	digitalRead(PUMP_RLY)				0	1	Pump Relay State
13	R	bool	digitalRead(VALVE_RLY)				0	1	Valve Relay State
14	R	bool	digitalRead(COMPRESSOR_RLY)				0	1	Compressor State
15	R/W	uint8_t	reservoir_setpoint	°C			0	100	Reservoir Temp Setpoint
16	R/W	uint8_t	hysteresis	°C			0	100	Reservoir Temp Hysteresis
17	R	uint32_t	last_compressor	ms			0		Last Compressor Time
18	R/W	uint32_t	compressor_lockout	ms			0		Compressor Lockout Time
19	R	uint32_t	last_valve	ms			0		Last Valve Time
20	R/W	uint32_t	valve_lockout	ms			0		Valve Lockout Time
21	W	bool					0	1	Start Cooling
22	W	bool					0	1	Stop Cooling
23	R/W	uint8_t	reservoir_temp_high_limit	°C			0	100	Reservoir Temperature High Limit
24	R/W	uint8_t	reservoir_temp_low_limit	°C			0	100	Reservoir Temperature Low Limit
25	R/W	uint8_t	outside_temp_high_limit	°C			0	100	Outside Temperature High Limit
26	R/W	uint8_t	outside_temp_low_limit	°C			0	100	Outside Temperature Low Limit
27	R/W	uint8_t	case_temperature_high_limit	°C			0	100	Case Temperature High Limit
28	R/W	uint8_t	case_temperature_low_limit	°C			0	100	Case Temperature Low Limit
29	R/W	uint8_t	case_humidity_high_limit	%RH			0	100	Case Humidity High Limit
30	R/W	uint16_t	filter_high_limit	ADC			0	1024	Filter Delta P High Limit
31	R/W	uint16_t	reservoir_volume_low_limit	mL			0	6000	Reservoir Level Low Limit